## Cond Unit MT - Fix CAP+Stepless
Condensing Unit (MT) − Fix Capacity or Stepless Capacity Control | [6 empty] | Tool version 1.4.2_rev06.16 | 2016-06-18
Declared cooling capacity at full load i.e. Point A (DC, in kW) |  |  | 7
[6 empty] | Degradation Calculation |  |  | Need to be filled in
|  | Cooling demand (PR) | DC in kW (measured or calculated) | COP at this DC (measured or calculated) | Degradation coefficient Cd | Capacity Ratio CR | COP at Part Load COP(PL) |  | Automatically filled in
| COP | (=DC(full load)*Partload) |  |  |  | (=PR/DC) | (=COP@full cap)*(1-Cd*(1-CR)) |  | Strasbourg temperature profile
COP A | 2.1 | 7 | 7 | 2.1 | 0.25 | 1 | 2.1 |  | Use default for Cd or measured value if verified by test
COP B | 2.57 | 6.2741 | 7.76 | 2.57 | 0.25 | 0.80851 | 2.447
COP C | 3.27 | 5.237 | 8.74 | 3.27 | 0.25 | 0.5992 | 2.9423 |  | For frther information see
COP D | 4 | 4.2 | 9.61 | 4 | 0.25 | 0.43704 | 3.437 |  | "ReadMe" page
| j | Tj (°C) | hj | partload% | refrigeration demand | COPPL | Ph*Tj | PH*Tj/COPDC | COP at part load for fix capacity units:
| 1 | -19 | 0.083351 | 60% | 4.2 | 3.437 | 0.35008 | 0.10185 | Calculation according to prEN13215:2015, Annex A
| 2 | -18 | 0.40727 | 60% | 4.2 | 3.437 | 1.7105 | 0.49768
| 3 | -17 | 0.64624 | 60% | 4.2 | 3.437 | 2.7142 | 0.7897
| 4 | -16 | 1.0535 | 60% | 4.2 | 3.437 | 4.4248 | 1.2874
| 5 | -15 | 1.7412 | 60% | 4.2 | 3.437 | 7.313 | 2.1277
| 6 | -14 | 2.9786 | 60% | 4.2 | 3.437 | 12.5101 | 3.6398
| 7 | -13 | 3.793 | 60% | 4.2 | 3.437 | 15.9306 | 4.635
| 8 | -12 | 5.6854 | 60% | 4.2 | 3.437 | 23.8787 | 6.9475 | Degradation Coefficient (Cd) at part load for fix capacity units:
| 9 | -11 | 8.937 | 60% | 4.2 | 3.437 | 37.5355 | 10.9209 | Since condensing units are no functional system Cd can not be determined by test.
| 10 | -10 | 11.8115 | 60% | 4.2 | 3.437 | 49.6083 | 14.4334 | For this case the default degradation coefficient Cd shall be 0.25.
| 11 | -9 | 17.2861 | 60% | 4.2 | 3.437 | 72.6017 | 21.1233
| 12 | -8 | 20.0184 | 60% | 4.2 | 3.437 | 84.0774 | 24.4621
| 13 | -7 | 28.7314 | 60% | 4.2 | 3.437 | 120.6717 | 35.1091
| 14 | -6 | 39.7062 | 60% | 4.2 | 3.437 | 166.7658 | 48.5201
| 15 | -5 | 56.6131 | 60% | 4.2 | 3.437 | 237.7749 | 69.18
| 16 | -4 | 76.3625 | 60% | 4.2 | 3.437 | 320.7224 | 93.3134
| 17 | -3 | 106.0655 | 60% | 4.2 | 3.437 | 445.4753 | 129.61
| 18 | -2 | 153.222 | 60% | 4.2 | 3.437 | 643.5325 | 187.2342
| 19 | -1 | 203.4136 | 60% | 4.2 | 3.437 | 854.3371 | 248.5673
| 20 | 0 | 247.9751 | 60% | 4.2 | 3.437 | 1041.4954 | 303.0206
| 21 | 1 | 282.0066 | 60% | 4.2 | 3.437 | 1184.4277 | 344.6064
| 22 | 2 | 275.9131 | 60% | 4.2 | 3.437 | 1158.8351 | 337.1603
| 23 | 3 | 300.6113 | 60% | 4.2 | 3.437 | 1262.5673 | 367.341
| 24 | 4 | 310.7673 | 60% | 4.2 | 3.437 | 1305.2227 | 379.7515
D | 25 | 5 | 336.4773 | 60% | 4.2 | 3.437 | 1413.2049 | 411.1686
| 26 | 6 | 350.4772 | 61.48% | 4.3037 | 3.3876 | 1508.3501 | 445.2595
| 27 | 7 | 363.4945 | 62.96% | 4.4074 | 3.3381 | 1602.0682 | 479.9334
| 28 | 8 | 368.9063 | 64.44% | 4.5111 | 3.2886 | 1664.1773 | 506.0388
| 29 | 9 | 371.6343 | 65.93% | 4.6148 | 3.2392 | 1715.0236 | 529.4645
| 30 | 10 | 377.3222 | 67.41% | 4.7185 | 3.1897 | 1780.4016 | 558.1727
| 31 | 11 | 376.5281 | 68.89% | 4.8222 | 3.1402 | 1815.702 | 578.2072
| 32 | 12 | 386.4212 | 70.37% | 4.9259 | 3.0908 | 1903.482 | 615.8626
| 33 | 13 | 389.843 | 71.85% | 5.0296 | 3.0413 | 1960.7659 | 644.7157
| 34 | 14 | 384.448 | 73.33% | 5.1333 | 2.9918 | 1973.4996 | 659.6322
C | 35 | 15 | 370.4541 | 74.81% | 5.237 | 2.9423 | 1940.082 | 659.3651
| 36 | 16 | 344.9639 | 76.3% | 5.3407 | 2.8928 | 1842.3626 | 636.8763
| 37 | 17 | 328.0247 | 77.78% | 5.4444 | 2.8433 | 1785.9125 | 628.1185
| 38 | 18 | 305.3627 | 79.26% | 5.5481 | 2.7937 | 1694.1973 | 606.4273
| 39 | 19 | 261.8688 | 80.74% | 5.6519 | 2.7442 | 1480.0436 | 539.3357
| 40 | 20 | 223.8986 | 82.22% | 5.7556 | 2.6947 | 1288.6609 | 478.2277
| 41 | 21 | 196.3056 | 83.7% | 5.8593 | 2.6451 | 1150.2056 | 434.8403
| 42 | 22 | 163.0446 | 85.19% | 5.963 | 2.5956 | 972.2287 | 374.5703
| 43 | 23 | 141.7763 | 86.67% | 6.0667 | 2.546 | 860.1098 | 337.8217
| 44 | 24 | 121.9296 | 88.15% | 6.1704 | 2.4965 | 752.3506 | 301.3611
B | 45 | 25 | 104.4601 | 89.63% | 6.2741 | 2.447 | 655.3904 | 267.8375
| 46 | 26 | 85.7688 | 91.11% | 6.3778 | 2.3974 | 547.0144 | 228.1695
| 47 | 27 | 71.5382 | 92.59% | 6.4815 | 2.3478 | 463.6735 | 197.4897
| 48 | 28 | 56.5744 | 94.07% | 6.5852 | 2.2983 | 372.5528 | 162.1015
| 49 | 29 | 43.3482 | 95.56% | 6.6889 | 2.2487 | 289.951 | 128.9415
| 50 | 30 | 31.024 | 97.04% | 6.7926 | 2.1991 | 210.7335 | 95.8257
| 51 | 31 | 20.2062 | 98.52% | 6.8963 | 2.1496 | 139.3477 | 64.8259
A | 52 | 32 | 11.8503 | 100% | 7 | 2.1 | 82.9523 | 39.5011
| 53 | 33 | 8.1679 | 100% | 7 | 2.1 | 57.1751 | 27.2262
| 54 | 34 | 3.8297 | 100% | 7 | 2.1 | 26.8076 | 12.7655
| 55 | 35 | 2.0914 | 100% | 7 | 2.1 | 14.6395 | 6.9712
| 56 | 36 | 1.2076 | 100% | 7 | 2.1 | 8.4529 | 4.0252
| 57 | 37 | 0.5218 | 100% | 7 | 2.1 | 3.6526 | 1.7393
| 58 | 38 | 0.40138 | 100% | 7 | 2.1 | 2.8097 | 1.3379
[6 empty] | total | 43032.4645 | 14298.537
[7 empty] | SEPR | 3.0096
DC = declared cooling capacity at temperatures A, B, C and D
Please consider: Selection of COPA, COPB, COPC, COPD depends on different ambient temp conditions, load profile and application temperature (MT, LT)
Ratio between refrigerant demand and declared capacity (CR=1, in case of a continuous capacity adjustment)
DC at rating points B, C and D shall not be lower than 97%
of the cooling demand (PR) -- CR < 1.03
COP
COP
Note on E8: COP A related to: 32°C ambient temperature -10°C evaporating temperature
Note on D9: DC B related to: 25°C ambient temperature -10°C evaporating temperature
Note on E9: COP B related to: 25°C ambient temperature -10°C evaporating temperature
Note on D10: DC C related to: 15°C ambient temperature -10°C evaporating temperature
Note on E10: COP C related to: 15°C ambient temperature -10°C evaporating temperature
Note on D11: DC D related to: 5°C ambient temperature -10°C evaporating temperature
Note on E11: COP D related to: 5°C ambient temperature -10°C evaporating temperature

## Cond Unit MT - Step CAP
Condensing Unit (MT) − Step Capacity Control | [6 empty] | Tool version 1.4.2_rev06.16 | 2016-06-18
Declared cooling capacity at full load i.e. Point A (DC, in kW) |  |  | 7
[8 empty] | Degradation Calculation |  |  | Need to be filled in
|  | Cooling demand (PR) | DC in kW (measured or calculated) | COP at this DC (measured or calculated) | DC at part load (measured or calculated) | COP at part load (measured or calculated) | Degradation coefficient Cd | Capacity Ratio CR | COP at Part Load COP(PL) |  | Automatically filled in
| COP | (=DC(full load)*Partload) | [5 empty] | (=PR/DC) | (=COP@full cap)*(1-Cd*(1-CR)) |  | Strasbourg temperature profile
COP A | 2.1 | 7 | 7 | 2.1 | − | − | 0.25 | 1 | 2.1 |  | Use default for Cd or measured value if verified by test
COP B | 2.57 | 6.2741 | 7.76 | 2.57 | 3.1 | 2.44 | 0.25 | 0.80851 | 2.5285
COP C | 3.27 | 5.237 | 8.74 | 3.27 | 3.5 | 3.1 | 0.25 | 0.5992 | 3.1564 |  | For frther information see
COP D | 4 | 4.2 | 9.61 | 4 | 3.84 | 3.8 | 0.25 | 0.43704 | 3.8125 |  | "ReadMe" page
| j | Tj (°C) | hj | partload% | refrigeration demand | COPPL | Ph*Tj | PH*Tj/COPDC
| 1 | -19 | 0.083351 | 60% | 4.2 | 3.8125 | 0.35008 | 0.091824
| 2 | -18 | 0.40727 | 60% | 4.2 | 3.8125 | 1.7105 | 0.44867
| 3 | -17 | 0.64624 | 60% | 4.2 | 3.8125 | 2.7142 | 0.71193
| 4 | -16 | 1.0535 | 60% | 4.2 | 3.8125 | 4.4248 | 1.1606 |  | COP at part load for fix capacity units:
| 5 | -15 | 1.7412 | 60% | 4.2 | 3.8125 | 7.313 | 1.9182 |  | Calculation according to prEN13215:2015, Annex A
| 6 | -14 | 2.9786 | 60% | 4.2 | 3.8125 | 12.5101 | 3.2814
| 7 | -13 | 3.793 | 60% | 4.2 | 3.8125 | 15.9306 | 4.1785
| 8 | -12 | 5.6854 | 60% | 4.2 | 3.8125 | 23.8787 | 6.2633
| 9 | -11 | 8.937 | 60% | 4.2 | 3.8125 | 37.5355 | 9.8454
| 10 | -10 | 11.8115 | 60% | 4.2 | 3.8125 | 49.6083 | 13.0121
| 11 | -9 | 17.2861 | 60% | 4.2 | 3.8125 | 72.6017 | 19.0432
| 12 | -8 | 20.0184 | 60% | 4.2 | 3.8125 | 84.0774 | 22.0532 |  | Degradation Coefficient (Cd) at part load for fix capacity units:
| 13 | -7 | 28.7314 | 60% | 4.2 | 3.8125 | 120.6717 | 31.6518 |  | Since condensing units are no functional system Cd can not be determined by test.
| 14 | -6 | 39.7062 | 60% | 4.2 | 3.8125 | 166.7658 | 43.7421 |  | For this case the default degradation coefficient Cd shall be 0.25.
| 15 | -5 | 56.6131 | 60% | 4.2 | 3.8125 | 237.7749 | 62.3675
| 16 | -4 | 76.3625 | 60% | 4.2 | 3.8125 | 320.7224 | 84.1244
| 17 | -3 | 106.0655 | 60% | 4.2 | 3.8125 | 445.4753 | 116.8466
| 18 | -2 | 153.222 | 60% | 4.2 | 3.8125 | 643.5325 | 168.7964
| 19 | -1 | 203.4136 | 60% | 4.2 | 3.8125 | 854.3371 | 224.0897
| 20 | 0 | 247.9751 | 60% | 4.2 | 3.8125 | 1041.4954 | 273.1807
| 21 | 1 | 282.0066 | 60% | 4.2 | 3.8125 | 1184.4277 | 310.6713
| 22 | 2 | 275.9131 | 60% | 4.2 | 3.8125 | 1158.8351 | 303.9585
| 23 | 3 | 300.6113 | 60% | 4.2 | 3.8125 | 1262.5673 | 331.1671
| 24 | 4 | 310.7673 | 60% | 4.2 | 3.8125 | 1305.2227 | 342.3554
D | 25 | 5 | 336.4773 | 60% | 4.2 | 3.8125 | 1413.2049 | 370.6788
| 26 | 6 | 350.4772 | 61.48% | 4.3037 | 3.7469 | 1508.3501 | 402.5631
| 27 | 7 | 363.4945 | 62.96% | 4.4074 | 3.6813 | 1602.0682 | 435.1964
| 28 | 8 | 368.9063 | 64.44% | 4.5111 | 3.6156 | 1664.1773 | 460.2717
| 29 | 9 | 371.6343 | 65.93% | 4.6148 | 3.55 | 1715.0236 | 483.1013
| 30 | 10 | 377.3222 | 67.41% | 4.7185 | 3.4844 | 1780.4016 | 510.9612
| 31 | 11 | 376.5281 | 68.89% | 4.8222 | 3.4188 | 1815.702 | 531.0928
| 32 | 12 | 386.4212 | 70.37% | 4.9259 | 3.3532 | 1903.482 | 567.6628
| 33 | 13 | 389.843 | 71.85% | 5.0296 | 3.2876 | 1960.7659 | 596.4164
| 34 | 14 | 384.448 | 73.33% | 5.1333 | 3.222 | 1973.4996 | 612.514
C | 35 | 15 | 370.4541 | 74.81% | 5.237 | 3.1564 | 1940.082 | 614.6592
| 36 | 16 | 344.9639 | 76.3% | 5.3407 | 3.0936 | 1842.3626 | 595.5451
| 37 | 17 | 328.0247 | 77.78% | 5.4444 | 3.0308 | 1785.9125 | 589.2559
| 38 | 18 | 305.3627 | 79.26% | 5.5481 | 2.968 | 1694.1973 | 570.8189
| 39 | 19 | 261.8688 | 80.74% | 5.6519 | 2.9052 | 1480.0436 | 509.4409
| 40 | 20 | 223.8986 | 82.22% | 5.7556 | 2.8425 | 1288.6609 | 453.3626
| 41 | 21 | 196.3056 | 83.7% | 5.8593 | 2.7797 | 1150.2056 | 413.7921
| 42 | 22 | 163.0446 | 85.19% | 5.963 | 2.7169 | 972.2287 | 357.8463
| 43 | 23 | 141.7763 | 86.67% | 6.0667 | 2.6541 | 860.1098 | 324.0673
| 44 | 24 | 121.9296 | 88.15% | 6.1704 | 2.5913 | 752.3506 | 290.334
B | 45 | 25 | 104.4601 | 89.63% | 6.2741 | 2.5285 | 655.3904 | 259.1964
| 46 | 26 | 85.7688 | 91.11% | 6.3778 | 2.4673 | 547.0144 | 221.7033
| 47 | 27 | 71.5382 | 92.59% | 6.4815 | 2.4061 | 463.6735 | 192.7071
| 48 | 28 | 56.5744 | 94.07% | 6.5852 | 2.3449 | 372.5528 | 158.879
| 49 | 29 | 43.3482 | 95.56% | 6.6889 | 2.2837 | 289.951 | 126.9675
| 50 | 30 | 31.024 | 97.04% | 6.7926 | 2.2224 | 210.7335 | 94.8207
| 51 | 31 | 20.2062 | 98.52% | 6.8963 | 2.1612 | 139.3477 | 64.4764
A | 52 | 32 | 11.8503 | 100% | 7 | 2.1 | 82.9523 | 39.5011
| 53 | 33 | 8.1679 | 100% | 7 | 2.1 | 57.1751 | 27.2262
| 54 | 34 | 3.8297 | 100% | 7 | 2.1 | 26.8076 | 12.7655
| 55 | 35 | 2.0914 | 100% | 7 | 2.1 | 14.6395 | 6.9712
| 56 | 36 | 1.2076 | 100% | 7 | 2.1 | 8.4529 | 4.0252
| 57 | 37 | 0.5218 | 100% | 7 | 2.1 | 3.6526 | 1.7393
| 58 | 38 | 0.40138 | 100% | 7 | 2.1 | 2.8097 | 1.3379
[6 empty] | total | 43032.4645 | 13276.8573
[7 empty] | SEPR | 3.2412
DC = declared cooling capacity at temperatures A, B, C and D
Please consider: Selection of COPA, COPB, COPC, COPD depends on different ambient temp conditions, load profile and application temperature (LT, MT)
Ratio between cooling demand and declared capacity (CR=1, in case of a continuous capacity adjustment)
Measured or calculated cooling capacity equal or above cooling demand
Measured or calculated part load capacity below cooling demand. Leave DC and COP blank if step control not available/necessary. Lowest part load DC limited to > 10% of DC at full load.
For step control, COP is a linear interpolation between the operating points above and below cooling demand
COP
COP
Note on E8: COP A related to: 32°C ambient temperature -10°C evaporating temperature
Note on D9: DC B related to: 25°C ambient temperature -10°C evaporating temperature
Note on E9: COP B related to: 25°C ambient temperature -10°C evaporating temperature
Note on F9: DC B related to: 25°C ambient temperature -10°C evaporating temperature
Note on G9: COP B related to: 25°C ambient temperature -10°C evaporating temperature
Note on D10: DC C related to: 15°C ambient temperature -10°C evaporating temperature
Note on E10: COP C related to: 15°C ambient temperature -10°C evaporating temperature
Note on F10: DC C related to: 15°C ambient temperature -10°C evaporating temperature
Note on G10: COP C related to: 15°C ambient temperature -10°C evaporating temperature
Note on D11: DC D related to: 5°C ambient temperature -10°C evaporating temperature
Note on E11: COP D related to: 5°C ambient temperature -10°C evaporating temperature
Note on F11: DC D related to: 5°C ambient temperature -10°C evaporating temperature
Note on G11: COP D related to: 5°C ambient temperature -10°C evaporating temperature

## Cond Unit LT - Fix Cap+Stepless
Condensing Unit (LT) − Fix Capacity or Stepless Capacity Control | [6 empty] | Tool version 1.4.2_rev06.16 | 2016-06-18
Declared cooling capacity at full load i.e. Point A (DC, in kW) |  |  | 5.25
[6 empty] | Degradation Calculation |  |  | Need to be filled in
|  | Cooling demand (PR) | DC in kW (measured or calculated) | COP at this DC (measured or calculated) | Degradation coefficient Cd | Capacity Ratio CR | COP at Part Load COP(PL) |  | Automatically filled in
| COP | (=DC(full load)*Partload) |  |  |  | (=PR/DC) | (=COP@full cap)*(1-Cd*(1-CR)) |  | Strasbourg temperature profile
COP A | 1.07 | 5.25 | 5.25 | 1.07 | 0.25 | 1 | 1.07 |  | Use default for Cd or measured value if verified by test
COP B | 1.28 | 4.9778 | 5.7 | 1.28 | 0.25 | 0.87329 | 1.2395
COP C | 1.63 | 4.5889 | 6.25 | 1.63 | 0.25 | 0.73422 | 1.5217 |  | For frther information see
COP D | 2.05 | 4.2 | 6.75 | 2.05 | 0.25 | 0.62222 | 1.8564 |  | "ReadMe" page
| j | Tj (°C) | hj | partload% | refrigeration demand | COPPL | Ph*Tj | PH*Tj/COPDC | COP at part load for fix capacity units:
| 1 | -19 | 0.083351 | 80% | 4.2 | 1.8564 | 0.35008 | 0.18858 | Calculation according to prEN13215:2015, Annex A
| 2 | -18 | 0.40727 | 80% | 4.2 | 1.8564 | 1.7105 | 0.92143
| 3 | -17 | 0.64624 | 80% | 4.2 | 1.8564 | 2.7142 | 1.4621
| 4 | -16 | 1.0535 | 80% | 4.2 | 1.8564 | 4.4248 | 2.3835
| 5 | -15 | 1.7412 | 80% | 4.2 | 1.8564 | 7.313 | 3.9394
| 6 | -14 | 2.9786 | 80% | 4.2 | 1.8564 | 12.5101 | 6.739
| 7 | -13 | 3.793 | 80% | 4.2 | 1.8564 | 15.9306 | 8.5815
| 8 | -12 | 5.6854 | 80% | 4.2 | 1.8564 | 23.8787 | 12.863 | Degradation Coefficient (Cd) at part load for fix capacity units:
| 9 | -11 | 8.937 | 80% | 4.2 | 1.8564 | 37.5355 | 20.2196 | Since condensing units are no functional system Cd can not be determined by test.
| 10 | -10 | 11.8115 | 80% | 4.2 | 1.8564 | 49.6083 | 26.723 | For this case the default degradation coefficient Cd shall be 0.25.
| 11 | -9 | 17.2861 | 80% | 4.2 | 1.8564 | 72.6017 | 39.1091
| 12 | -8 | 20.0184 | 80% | 4.2 | 1.8564 | 84.0774 | 45.2909
| 13 | -7 | 28.7314 | 80% | 4.2 | 1.8564 | 120.6717 | 65.0035
| 14 | -6 | 39.7062 | 80% | 4.2 | 1.8564 | 166.7658 | 89.8335
| 15 | -5 | 56.6131 | 80% | 4.2 | 1.8564 | 237.7749 | 128.0847
| 16 | -4 | 76.3625 | 80% | 4.2 | 1.8564 | 320.7224 | 172.7668
| 17 | -3 | 106.0655 | 80% | 4.2 | 1.8564 | 445.4753 | 239.9687
| 18 | -2 | 153.222 | 80% | 4.2 | 1.8564 | 643.5325 | 346.6582
| 19 | -1 | 203.4136 | 80% | 4.2 | 1.8564 | 854.3371 | 460.2145
| 20 | 0 | 247.9751 | 80% | 4.2 | 1.8564 | 1041.4954 | 561.033
| 21 | 1 | 282.0066 | 80% | 4.2 | 1.8564 | 1184.4277 | 638.0278
| 22 | 2 | 275.9131 | 80% | 4.2 | 1.8564 | 1158.8351 | 624.2416
| 23 | 3 | 300.6113 | 80% | 4.2 | 1.8564 | 1262.5673 | 680.12
| 24 | 4 | 310.7673 | 80% | 4.2 | 1.8564 | 1305.2227 | 703.0977
D | 25 | 5 | 336.4773 | 80% | 4.2 | 1.8564 | 1413.2049 | 761.2655
| 26 | 6 | 350.4772 | 80.74% | 4.2389 | 1.8229 | 1485.634 | 814.975
| 27 | 7 | 363.4945 | 81.48% | 4.2778 | 1.7895 | 1554.9485 | 868.9532
| 28 | 8 | 368.9063 | 82.22% | 4.3167 | 1.756 | 1592.4455 | 906.8695
| 29 | 9 | 371.6343 | 82.96% | 4.3556 | 1.7225 | 1618.674 | 939.7174
| 30 | 10 | 377.3222 | 83.7% | 4.3944 | 1.689 | 1658.1213 | 981.6932
| 31 | 11 | 376.5281 | 84.44% | 4.4333 | 1.6556 | 1669.2744 | 1008.276
| 32 | 12 | 386.4212 | 85.19% | 4.4722 | 1.6221 | 1728.1613 | 1065.3829
| 33 | 13 | 389.843 | 85.93% | 4.5111 | 1.5886 | 1758.6251 | 1107.0044
| 34 | 14 | 384.448 | 86.67% | 4.55 | 1.5552 | 1749.2383 | 1124.7928
C | 35 | 15 | 370.4541 | 87.41% | 4.5889 | 1.5217 | 1699.9729 | 1117.157
| 36 | 16 | 344.9639 | 88.15% | 4.6278 | 1.4935 | 1596.4161 | 1068.9298
| 37 | 17 | 328.0247 | 88.89% | 4.6667 | 1.4652 | 1530.7821 | 1044.7261
| 38 | 18 | 305.3627 | 89.63% | 4.7056 | 1.437 | 1436.901 | 999.915
| 39 | 19 | 261.8688 | 90.37% | 4.7444 | 1.4088 | 1242.4219 | 881.9015
| 40 | 20 | 223.8986 | 91.11% | 4.7833 | 1.3806 | 1070.9817 | 775.7505
| 41 | 21 | 196.3056 | 91.85% | 4.8222 | 1.3524 | 946.6294 | 699.988
| 42 | 22 | 163.0446 | 92.59% | 4.8611 | 1.3241 | 792.5777 | 598.5664
| 43 | 23 | 141.7763 | 93.33% | 4.9 | 1.2959 | 694.7041 | 536.0774
| 44 | 24 | 121.9296 | 94.07% | 4.9389 | 1.2677 | 602.1966 | 475.039
B | 45 | 25 | 104.4601 | 94.81% | 4.9778 | 1.2395 | 519.9792 | 419.5227
| 46 | 26 | 85.7688 | 95.56% | 5.0167 | 1.2152 | 430.2735 | 354.0627
| 47 | 27 | 71.5382 | 96.3% | 5.0556 | 1.191 | 361.6653 | 303.6554
| 48 | 28 | 56.5744 | 97.04% | 5.0944 | 1.1668 | 288.2151 | 247.0067
| 49 | 29 | 43.3482 | 97.78% | 5.1333 | 1.1426 | 222.5206 | 194.7453
| 50 | 30 | 31.024 | 98.52% | 5.1722 | 1.1184 | 160.4631 | 143.4736
| 51 | 31 | 20.2062 | 99.26% | 5.2111 | 1.0942 | 105.2965 | 96.2308
A | 52 | 32 | 11.8503 | 100% | 5.25 | 1.07 | 62.2142 | 58.1441
| 53 | 33 | 8.1679 | 100% | 5.25 | 1.07 | 42.8813 | 40.076
| 54 | 34 | 3.8297 | 100% | 5.25 | 1.07 | 20.1057 | 18.7904
| 55 | 35 | 2.0914 | 100% | 5.25 | 1.07 | 10.9797 | 10.2614
| 56 | 36 | 1.2076 | 100% | 5.25 | 1.07 | 6.3397 | 5.9249
| 57 | 37 | 0.5218 | 100% | 5.25 | 1.07 | 2.7394 | 2.5602
| 58 | 38 | 0.40138 | 100% | 5.25 | 1.07 | 2.1073 | 1.9694
[6 empty] | total | 39132.174 | 24550.8754
[7 empty] | SEPR | 1.5939
Ratio between refrigerant demand and declared capacity (=1, in case of a continuous capacity adjustment)
Please consider: Selection of COPA, COPB, COPC, COPD depends on different ambient temp conditions, load profile and application temperature (LT, MT)
DC = declared cooling capacity at temperatures A, B, C and D
DC at rating points B, C and D shall not be lower than 97%
of the cooling demand (PR) -- CR < 1.03
COP
COP
Note on E8: COP A related to: 32°C ambient temperature -35°C evaporating temperature
Note on D9: DC B related to: 25°C ambient temperature -35°C evaporating temperature
Note on E9: COP B related to: 25°C ambient temperature -35°C evaporating temperature
Note on D10: DC C related to: 15°C ambient temperature -35°C evaporating temperature
Note on E10: COP C related to: 15°C ambient temperature -35°C evaporating temperature
Note on D11: DC D related to: 5°C ambient temperature -35°C evaporating temperature
Note on E11: COP D related to: 5°C ambient temperature -35°C evaporating temperature

## Cond Unit LT - Step CAP
Condensing Unit (LT) − Step Capacity Control | [6 empty] | Tool version 1.4.2_rev06.16 | 2016-06-18
Declared cooling capacity at full load i.e. Point A (DC, in kW) |  |  | 5.25
[8 empty] | Degradation Calculation |  |  | Need to be filled in
|  | Cooling demand (PR) | DC in kW (measured or calculated) | COP at this DC (measured or calculated) | DC at part load (measured or calculated) | COP at part load (measured or calculated) | Degradation coefficient Cd | Capacity Ratio CR | COP at Part Load COP(PL) |  | Automatically filled in
| COP | (=DC(full load)*Partload) | [5 empty] | (=PR/DC) | (=COP@full cap)*(1-Cd*(1-CR)) |  | Strasbourg temperature profile
COP A | 1.07 | 5.25 | 5.25 | 1.07 | − | − | 0.25 | 1 | 1.07 |  | Use default for Cd or measured value if verified by test
COP B | 1.28 | 4.9778 | 5.7 | 1.28 | 2.85 | 1.22 | 0.25 | 0.87329 | 1.2648
COP C | 1.63 | 4.5889 | 6.25 | 1.63 | 3.15 | 1.55 | 0.25 | 0.73422 | 1.5871 |  | For frther information see
COP D | 2.05 | 4.2 | 6.75 | 2.05 | 3.4 | 1.95 | 0.25 | 0.62222 | 1.9739 |  | "ReadMe" page
"ReadMe" page
| j | Tj (°C) | hj | partload% | refrigeration demand | COPPL | Ph*Tj | PH*Tj/COPDC
| 1 | -19 | 0.083351 | 80% | 4.2 | 1.9739 | 0.35008 | 0.17735
| 2 | -18 | 0.40727 | 80% | 4.2 | 1.9739 | 1.7105 | 0.86658
| 3 | -17 | 0.64624 | 80% | 4.2 | 1.9739 | 2.7142 | 1.3751 |  | COP at part load for fix capacity units:
| 4 | -16 | 1.0535 | 80% | 4.2 | 1.9739 | 4.4248 | 2.2417 |  | Calculation according to prEN13215:2015, Annex A
| 5 | -15 | 1.7412 | 80% | 4.2 | 1.9739 | 7.313 | 3.7049
| 6 | -14 | 2.9786 | 80% | 4.2 | 1.9739 | 12.5101 | 6.3378
| 7 | -13 | 3.793 | 80% | 4.2 | 1.9739 | 15.9306 | 8.0707
| 8 | -12 | 5.6854 | 80% | 4.2 | 1.9739 | 23.8787 | 12.0973
| 9 | -11 | 8.937 | 80% | 4.2 | 1.9739 | 37.5355 | 19.0161
| 10 | -10 | 11.8115 | 80% | 4.2 | 1.9739 | 49.6083 | 25.1324
| 11 | -9 | 17.2861 | 80% | 4.2 | 1.9739 | 72.6017 | 36.7812 |  | Degradation Coefficient (Cd) at part load for fix capacity units:
| 12 | -8 | 20.0184 | 80% | 4.2 | 1.9739 | 84.0774 | 42.595 |  | Since condensing units are no functional system Cd can not be determined by test.
| 13 | -7 | 28.7314 | 80% | 4.2 | 1.9739 | 120.6717 | 61.1342 |  | For this case the default degradation coefficient Cd shall be 0.25.
| 14 | -6 | 39.7062 | 80% | 4.2 | 1.9739 | 166.7658 | 84.4863
| 15 | -5 | 56.6131 | 80% | 4.2 | 1.9739 | 237.7749 | 120.4606
| 16 | -4 | 76.3625 | 80% | 4.2 | 1.9739 | 320.7224 | 162.4832
| 17 | -3 | 106.0655 | 80% | 4.2 | 1.9739 | 445.4753 | 225.685
| 18 | -2 | 153.222 | 80% | 4.2 | 1.9739 | 643.5325 | 326.024
| 19 | -1 | 203.4136 | 80% | 4.2 | 1.9739 | 854.3371 | 432.821
| 20 | 0 | 247.9751 | 80% | 4.2 | 1.9739 | 1041.4954 | 527.6385
| 21 | 1 | 282.0066 | 80% | 4.2 | 1.9739 | 1184.4277 | 600.0503
| 22 | 2 | 275.9131 | 80% | 4.2 | 1.9739 | 1158.8351 | 587.0847
| 23 | 3 | 300.6113 | 80% | 4.2 | 1.9739 | 1262.5673 | 639.6371
| 24 | 4 | 310.7673 | 80% | 4.2 | 1.9739 | 1305.2227 | 661.2471
D | 25 | 5 | 336.4773 | 80% | 4.2 | 1.9739 | 1413.2049 | 715.9526
| 26 | 6 | 350.4772 | 80.74% | 4.2389 | 1.9352 | 1485.634 | 767.6878
| 27 | 7 | 363.4945 | 81.48% | 4.2778 | 1.8965 | 1554.9485 | 819.8909
| 28 | 8 | 368.9063 | 82.22% | 4.3167 | 1.8579 | 1592.4455 | 857.1414
| 29 | 9 | 371.6343 | 82.96% | 4.3556 | 1.8192 | 1618.674 | 889.7815
| 30 | 10 | 377.3222 | 83.7% | 4.3944 | 1.7805 | 1658.1213 | 931.2638
| 31 | 11 | 376.5281 | 84.44% | 4.4333 | 1.7418 | 1669.2744 | 958.3442
| 32 | 12 | 386.4212 | 85.19% | 4.4722 | 1.7032 | 1728.1613 | 1014.6812
| 33 | 13 | 389.843 | 85.93% | 4.5111 | 1.6645 | 1758.6251 | 1056.5599
| 34 | 14 | 384.448 | 86.67% | 4.55 | 1.6258 | 1749.2383 | 1075.9198
C | 35 | 15 | 370.4541 | 87.41% | 4.5889 | 1.5871 | 1699.9729 | 1071.0969
| 36 | 16 | 344.9639 | 88.15% | 4.6278 | 1.5549 | 1596.4161 | 1026.7009
| 37 | 17 | 328.0247 | 88.89% | 4.6667 | 1.5227 | 1530.7821 | 1005.3308
| 38 | 18 | 305.3627 | 89.63% | 4.7056 | 1.4904 | 1436.901 | 964.0839
| 39 | 19 | 261.8688 | 90.37% | 4.7444 | 1.4582 | 1242.4219 | 852.0257
| 40 | 20 | 223.8986 | 91.11% | 4.7833 | 1.426 | 1070.9817 | 751.058
| 41 | 21 | 196.3056 | 91.85% | 4.8222 | 1.3937 | 946.6294 | 679.2056
| 42 | 22 | 163.0446 | 92.59% | 4.8611 | 1.3615 | 792.5777 | 582.1372
| 43 | 23 | 141.7763 | 93.33% | 4.9 | 1.3293 | 694.7041 | 522.6236
| 44 | 24 | 121.9296 | 94.07% | 4.9389 | 1.297 | 602.1966 | 464.2892
B | 45 | 25 | 104.4601 | 94.81% | 4.9778 | 1.2648 | 519.9792 | 411.1172
| 46 | 26 | 85.7688 | 95.56% | 5.0167 | 1.237 | 430.2735 | 347.8454
| 47 | 27 | 71.5382 | 96.3% | 5.0556 | 1.2091 | 361.6653 | 299.1096
| 48 | 28 | 56.5744 | 97.04% | 5.0944 | 1.1813 | 288.2151 | 243.9789
| 49 | 29 | 43.3482 | 97.78% | 5.1333 | 1.1535 | 222.5206 | 192.9117
| 50 | 30 | 31.024 | 98.52% | 5.1722 | 1.1257 | 160.4631 | 142.5508
| 51 | 31 | 20.2062 | 99.26% | 5.2111 | 1.0978 | 105.2965 | 95.9135
A | 52 | 32 | 11.8503 | 100% | 5.25 | 1.07 | 62.2142 | 58.1441
| 53 | 33 | 8.1679 | 100% | 5.25 | 1.07 | 42.8813 | 40.076
| 54 | 34 | 3.8297 | 100% | 5.25 | 1.07 | 20.1057 | 18.7904
| 55 | 35 | 2.0914 | 100% | 5.25 | 1.07 | 10.9797 | 10.2614
| 56 | 36 | 1.2076 | 100% | 5.25 | 1.07 | 6.3397 | 5.9249
| 57 | 37 | 0.5218 | 100% | 5.25 | 1.07 | 2.7394 | 2.5602
| 58 | 38 | 0.40138 | 100% | 5.25 | 1.07 | 2.1073 | 1.9694
[6 empty] | total | 39132.174 | 23464.0766
[7 empty] | SEPR | 1.6677
DC = declared cooling capacity at temperatures A, B, C and D
Please consider: Selection of COPA, COPB, COPC, COPD depends on different ambient temp conditions, load profile and application temperature (LT, MT)
Measured or calculated cooling capacity equal or above cooling demand
Ratio between refrigerant demand and declared capacity (CR=1, in case of a continuous capacity adjustment)
Measured or calculated part load capacity below cooling demand. Leave DC and COP blank if step control not available/necessary. Lowest part load DC limited to > 10% of DC at full load.
For step control, COP is a linear interpolation between the operating points above and below cooling demand
COP
COP
Note on E8: COP A related to: 32°C ambient temperature -35°C evaporating temperature
Note on D9: DC B related to: 25°C ambient temperature -35°C evaporating temperature
Note on E9: COP B related to: 25°C ambient temperature -35°C evaporating temperature
Note on F9: DC B related to: 25°C ambient temperature -35°C evaporating temperature
Note on G9: COP B related to: 25°C ambient temperature -35°C evaporating temperature
Note on D10: DC C related to: 15°C ambient temperature -35°C evaporating temperature
Note on E10: COP C related to: 15°C ambient temperature -35°C evaporating temperature
Note on F10: DC C related to: 15°C ambient temperature -35°C evaporating temperature
Note on G10: COP C related to: 15°C ambient temperature -35°C evaporating temperature
Note on D11: DC D related to: 5°C ambient temperature -35°C evaporating temperature
Note on E11: COP D related to: 5°C ambient temperature -35°C evaporating temperature
Note on F11: DC D related to: 5°C ambient temperature -35°C evaporating temperature
Note on G11: COP D related to: 5°C ambient temperature -35°C evaporating temperature

## ReadMe
Tool version 1.4.2_rev06.16
2016-06-18
About this calculation tool
This calculation tool is provided to help suppliers to calculate the Seasonal Energy Performance Ratio (SEPR) for their products based upon 4 rating point measurements (or calculations) of COP.
It is intended to assist suppliers to assess the seasonal performance of their products according to a methodology that is to be used under the proposed European ecodesign regulation for condensing units.
This tool is provided free of charge and in good faith but without guarantee of accuracy. Users should satisfy themselves that the output meets the requirements of EU Regulation No. 2015/1095. Calculation methodology is based on prEN13215:2015 Annex A.
Temperature References (°C):
What is SEPR? Seasonal Energy Performance Ratio |  |  | A | B | C | D
SEPR is the seasonal energy performance ratio of a condensing unit. It is calculated from the COP of the condensing unit at 4 different ambient temperatures (see table) and cooling loads, called rating points. The required rating points are specified in prEN13215:2015, Annex A, showing for each rating point the necessary part load ratio and condenser inlet air dry bulb temperature. Ambient temperature references see table. | AIR (inlet) |  | 32 | 25 | 15 | 5
| Evaporation | MT | -10 | -10 | -10 | -10
How to use the tool |  | LT | -35 | -35 | -35 | -35
Due to different load profiles for MT and LT conditions there are in total four sheets for SEPR calculation: Two each for fixed capacity and stepless condensing units and two more for stepped capacity condensing units. Use the one appropriate to the condensing unit.
To use the spreadsheet:
1. Please insert the full load rated capacity in cell D3,
2. AND THEN declared rated capacity at the 3 part load rating points (B, C and D - cells D9:11)
3. Insert the declared COP at 4 rating points (cells E8:11).
4. In case of step capacity control also insert part load DC and COP at 3 rating points (B, C, D - cells F9:F11 and G9:G11)
The spreadsheet then calculates the SEPR automatically using a linear interpolation between the rating points A, B, C, and D and an assumption of a constant capacity for temperatures above A and below D.